## risk log
Project Risk Log Rev 06 dated 28 June 2007
[11 empty] | Qty of Risks at level | Total Approx £ impact of Risks at level
|  |  | Project Number: | HXLY0606 | Project Title: Quantum Coherence |  |  |  |  | Red | 5 | 70000
|  |  | Project Manager: | Kevin Barnes | College Customers / Business Contacts: |  |  |  |  | Amber | 2 | 0
|  |  | Project Board: | Dr Roy Burns plus appointed academics | [5 empty] | Green | 14 | 5000
ID | TYPE | AUTHOR | OWNER (i.e. A.Nother) | DATE IDENTIFIED | DESCRIPTION | PROB | IMPACT | LEVEL | APPROX IMPACT £ | STATUS | ACTION | Comments / Indications / Updates | LAST UPDATED
1 | Project | R. Hall | R. Hall | 2007-04-12 | Existing Ventilation insufficient for new design, new AHU Plant required. | 4 | 4 | 16 | 0 | Open | Contingency | Works to be designed to minimise impact on the surrounding areas | 2007-04-20 | red¦Open | notamber | notgreen | 0
2 | Project | R. Hall | R. Hall | 2007-04-12 | Existing LTHW supply insufficient to meet new requirements, additional heating plant required | 2 | 4 | 8 | 0 | Open | Contingency | Should be designed out | 2007-04-20 | notred | notamber | green¦Open | 0
3 | Project | R. Hall | R. Hall | 2007-04-12 | Insufficient room for process cooling plant within room | 1 | 4 | 4 | 0 | Open | Reduction | Should be designed out | 2007-04-20 | notred | notamber | green¦Open | 0
4 | Project | R. Hall | R. Hall | 2007-04-12 | Insufficient L0 drainage | 4 | 4 | 16 | 0 | Open | Acceptance | Pumping options not acceptable. Insurance cover required for involved risk | 2007-04-20 | red¦Open | notamber | notgreen | 0
5 | Project | R. Hall | R. Hall | 2007-04-12 | Existing services interfering with design expectation of final layout, leading to loss of ceiling height due to services. | 4 | 4 | 16 | 0 | Open | Reduction | Keep reduced ceiling height to minimum. Nil cost as end user spatial risk. | 2007-04-20 | red¦Open | notamber | notgreen | 0
6 | Project | R. Hall | R. Hall | 2007-04-12 | Works causing interference (dust / dirt) with surrounding sensitive areas. Specifically Laboratories 009A and B. | 4 | 4 | 16 | 0 | Open | Reduction | Extensive protection and planning required. To be covered by Contractors insurance. | 2007-05-21 | red¦Open | notamber | notgreen | 0
7 | Project | R. Hall | R. Hall | 2007-04-12 | Smoke Extract requirements impeding on proposed design. | 3 | 4 | 12 | 0 | Open | Reduction | Fire Officer to advise re: Smoke Ext grilles. Nil cost as end user spatial risk. | 2007-04-20 | notred | amber¦Open | notgreen | 0
8 | Project | R. Hall | R. Hall | 2007-04-12 | Lack of available electrical supply, new incoming main may be required | 1 | 1 | 1 | 0 | Open | Contingency | Survey beng carried out 20 April re: upgrading to current standards. Defined scope should be available to allow costing. No longer a risk. | 2007-04-20 | notred | notamber | green¦Open | 0
9 | Project | R. Hall | R. Hall | 2007-04-12 | Lack of available data and telephone capacity, ICT to upgrade existing system | 2 | 2 | 4 | 0 | Open | Contingency | Should be designed out | 2007-04-20 | notred | notamber | green¦Open | 0
10 | Project | R. Hall | Project Team | 2007-04-12 | Insufficient floor space for electrical distribution equipment | 2 | 4 | 8 | 0 | Open | Prevention | All building services and associated equipment to be sited as high as possible on walls. Nil cost as end user spatial risk. | 2007-04-20 | notred | notamber | green¦Open | 0
11 | Project | R. Hall | Project Team | 2007-04-12 | Insufficient wall space for mechanical services, services impede on work space | 4 | 3 | 12 | 0 | Open | Reduction | All building services and associated equipment to be sited as high as possible on walls. Nil cost as end user spatial risk. | 2007-04-20 | notred | amber¦Open | notgreen | 0
12 | Project | BMJ Arch | Project Team | 2007-04-16 | Existing services to be isolated | 1 | 1 | 1 | 0 | Open |  | Low risk as services are at "end of runs" | 2007-04-20 | notred | notamber | green¦Open | 0
13 | Project | BMJ Arch | Project Team | 2007-04-16 | Slips, Trips and Fall hazards | 1 | 3 | 3 | 0 | Open |  | Method Statements to cover for all potentioal dangers and avoidances. Contractors risk no cost. | 2007-04-20 | notred | notamber | green¦Open | 0
14 | Project | BMJ Arch | Project Team | 2007-04-16 | Confined space working | 1 | 1 | 1 | 0 | Open |  | Area between Blackett / Huxley Buildings, should be able to be costed within Budget. | 2007-04-20 | notred | notamber | green¦Open | 0
15 | Project | BMJ Arch | Project Team | 2007-04-16 | Removal of existing floor slab and balustrade | 2 | 3 | 6 | 0 | Open |  | Defined route for removing to be established. Method Statements to ensure practicabiltiyof minimising noise / dust / double bagging etc. | 2007-04-20 | notred | notamber | green¦Open | 0
16 | Project | BMJ Arch | Project Team | 2007-04-16 | Access issues for plant and materials | 4 | 2 | 8 | 0 | Open |  | Project Team to check if pavement light can be removed to assist in entry / exit for paltn / material / spoil etc. | 2007-04-20 | notred | notamber | green¦Open | 0
17 | Project | BMJ Arch | Project Team | 2007-04-16 | Spatial problems with temp works / scaffolding within 009 | 4 | 4 | 16 | 0 | Open |  | Method Statements to cover for all potentioal dangers and avoidances. Contractors risk no cost. | 2007-06-26 | red¦Open | notamber | notgreen | 0
18 | Project | BMJ Arch | Project Team | 2007-04-16 | Exisiting drains affected by chemical / other waste | 1 | 2 | 2 | 0 | Open |  | Should be designed out. Flushing agents to be used if required. System works currently so no rectification works required. | 2007-04-20 | notred | notamber | green¦Open | 0
19 | Project | BMJ Arch | Project Team | 2007-04-16 | Deleterious materials in existing construction | 3 | 2 | 6 | 5000 | Open |  | Some known to exist. Others may be discovered. Could effect time as well as cost. | 2007-04-20 | notred | notamber | green¦Open | 5000
20 | Project | BMJ Arch | Project Team | 2007-04-16 | Fumes associated with self levelling screeds / moisture supressant layer | 2 | 3 | 6 | 0 | Open |  | Specifications of finsihes to be low odour / provision of temporary extract to be installed if required. Can be costed in budget. | 2007-04-20 | notred | notamber | green¦Open | 0
21 | Project | BMJ Arch | Project Team | 2007-04-16 | Fumes associated with paints, lacquers etc | 2 | 2 | 4 | 0 | Open |  | Specifications of finsihes to be low odour / provision of temporary extract to be installed if required. Can be costed in budget. | 2007-04-20 | notred | notamber | green¦Open | 0
22 | Project | BMJ Arch | Project Team | 2007-04-16 | Fumes associated with floor finishes, adhesives etc | 2 | 3 | 6 | 0 | Open |  | Specifications of finsihes to be low odour / provision of temporary extract to be installed if required. Can be costed in budget. | 2007-04-20 |  |  |  | 0
23 | Project | BMJ Arch | Project Team | 2007-04-16 | General dust, noise and vibration | 2 | 3 | 6 | 0 | Open | Prevention | Use appropriate noise suppressors and strict Working Rules / Guidlelines. Consider - a) diamond sawing close to edge of the existing balcony to avoid using breakers if possible b) removal of materials through pavement light / grille opening. | 2007-04-20 |  |  |  | 0
24 | Project | BMJ Arch | Project Team | 2007-04-16 | Power floating concrete floors | 2 | 2 | 4 | 0 | Open | Prevention | Use appropriate noise suppressors and strict Working Rules / Guidelines | 2007-04-20 |  |  |  | 0
25 | Project | K. Barnes | Project Team | 2007-04-18 | Available funding insufficient for User requirements | 4 | 4 | 16 | N/A | Open | Reduction | Confirm indicative costs ASAP and ensure additional changes are minimised. Ascertain potential for additional funding through either College, Department or Grant money. | 2007-04-20
26 | Project | K. Barnes | Project Team | 2007-04-18 | Works restricted due to ongoing neighbouring projects and examinations | 4 | 4 | 16 | 20000 | Open | Reduction | Ensure programming incorporates all required restrictions on noise periods and access to site. Risk allowance includes for unforeseen changes | 2007-04-20
27 | Project | K. Barnes | Project Team | 2007-04-18 | Structural restrictions to proposed works | 3 | 4 | 12 |  | Open | Reduction | Structural engineers to complete detailed surveys and proposals are to minimise impact on the structure. Particular attention is to be paid to any required drainage. | 2007-04-20
28 | Business | D&S | Director | 2007-04-19 | Damage to equipment during decanting / return | 2 | 3 | 6 | 0 | Open |  | Medium risk to be covered by insurance | 2007-04-20
29 | Project | D&S | Project Team | 2007-04-19 | Late commencement / Delay to completion date | 3 | 4 | 12 | TBA | Open |  | ICL to confirm effect if project is handed over late. Will LAD's be sought ? Risk of losing funding in part if project passes critical date of March. | 2007-04-20
30 | Project | D&S | Project Team | 2007-04-19 | Design risks; i.e. routing of services, duties of exisiting, access / delivery issues all affecting cost certainty. | 4 | 4 | 16 | 50000 | Open |  | Ensure all access procedures, design issues, decanting etc and contract documents are finalised prior to commencement of the Works. Variations to design WILL be necessary. Changes to working patterns, available hours, structural / service route changes, equipment changes, additional items, End user requirements, etc. | 2007-04-20
31 | Project | All | Project Team | 2007-04-20 | Information on existing structure missing which may lead to discovery of problematic areas / works post contract. | 2 | 3 | 6 |  |  |  | Covered in part by Risk 30 | 2007-04-20
32 | Project | All | Project Team | 2007-04-20 | Lack of acoustic treatment | 2 | 2 | 4 | TBA |  |  | End user clarification required (KB to advise) | 2007-04-20
33 | Project | Curtins | P.Rogers | 2007-04-20 | Alterations carried out on the upper floor levels that affect the overall loading in the area under consideration | 2 | 3 | 6 | 0 | Open | Contingency | Client to confirm if any works have been carried out | 2007-04-25
34 | Project | Curtins | P.Rogers | 2007-04-20 | Existing structure to be confirmed. | 2 | 3 | 6 | 0 | Open |  | Existing drawings to be checked and opening up to be carried out where necessary | 2007-04-25
35 | Project | Curtins | Team | 2007-04-20 | Installation of materials - heavy beams, pumped concrete, etc. | 3 | 3 | 9 | 0 | Open | Reduction | Consider using pavemnt light / grille openings for installation. | 2007-04-25
INSERT NEW RISK ABOVE

## drop downs
TYPE | PROBABILITY | IMPACT | STATUS | ACTION
Business | 1 | 1 | Open | Contingency
Project | 2 | 2 | Closed | Transference
Stage | 3 | 3 |  | Prevention
| 4 | 4 |  | Reduction
Acceptance